## Slide 1: Herefordshire Health & Safety Group
ZOOM SEMINAR
10:00am Wednesday 24th March 2021
‘COVID Slippage – Things you might have missed’
Q&A Session
Housekeeping:
Please keep microphones ‘muted’ unless you wish to speak (this keeps down background noise).
Please ask questions though the ‘chat’ button.
Technical issues, please email info@herefordhsg.co.uk
Please note the Seminar will be recorded and may be used for supporting the communication of H&S advice.

## Slide 2
Asbestos
Electrical
Emergency Lighting
Fire
First Aid Equipment
Fuel Oil Storage
Gas Appliances: Boilers, Ovens Etc
Gas Cylinders
Lifts and Hoists
Lightning Conductors
Local Exhaust Ventilation
Dust Extraction Etc
Pressure Vessels
Compressors, Calorifiers And Air Receivers Etc
Water System Testing
Work at Height
Health and Safety Testing/ Inspection Requirements
The following is not an exhaustive list of all testing or inspection requirements but shows the key areas for which compliance would be sought the by either the HSE or insurers

## Slide 3
AREA | BY WHOM | Period of inspection/ Review | Comments
Asbestos | Management Survey by competent person Requirements of survey can be done in house with suitably trained employee | Check management plan to determine inspection frequency Generally Annually as a minimum | Statutory - Control of Asbestos Regulations 2012 (CAR) Visual inspection of asbestos remaining in situ can be recorded on site specific management plan Ensure asbestos permission is completed on each and every occasion work is undertaken where asbestos is presumed present. This applies equally to work undertaken in house or by contractors
ELECTRICAL: PAT TESTING | In House if member of staff PAT trained | Variable see HSE guidelines for more details | Advisory under PUWER, HSWA, Electricity at Work, Management regs Checking earthed equipment with a tester to ensure integrity of earth bonding and/or insulation. Inspection of cables, plugs fuses etc and of double-insulated equipment. Period for inspection is dependent upon the type of equipment and environment in which it is used.
ELECTRICAL: Fixed Electrical Installations (Fixed Wire Testing) |  | Minimum ONE, THREE or FIVE YEARLY testing of all fixed wiring and distribution boards depending on type of business | Statutory under Electricity at work regs 1989 The Electricity at Work Regulations 1989 state that “all systems shall be maintained so as to prevent, so far as is reasonably practicable, such danger.” This explicitly places a requirement on the employer to maintain electrical systems adequately in order to protect employees, visitors and other users of the space. It does not have to be done all at once but can be spread over the period for example doing 20% of the total every year over 5 years. Normally the time period will be suggested by your insurers and if you have any doubts ask them for advice
Emergency Lighting | Outside Contractor In house | Full test ANNUALLY Flick test MONTHLY | Statutory - Regulatory reform (Fire Safety) Order 2005 To demonstrate compliance emergency lighting must undergo a full test once a year, and be 'flick-tested' at least once a month. The main purpose of this kind of lighting is to illuminate escape routes, although it also allows occupants to find fire-fighting equipment if there's a fire.

## Slide 4
AREA | BY WHOM | Period of inspection/ Review | Comments
Fire Alarm Service | Outside Contractor | ANNUALLY For 230 volt systems without battery back up | Statutory - Regulatory reform (Fire Safety) Order 2005 Test and examination by competent service engineer
Fire Alarm Service | Outside Contractor | Six Monthly For systems with battery back up | Statutory - Regulatory reform (Fire Safety) Order 2005 Six monthly battery check, test and examination by competent service engineer This check may also include 50% of the automatic smoke / heat detectors, sounders and manually operated devices
Fire Alarm Testing | IN HOUSE | DAILY WEEKLY Check alarm is audible in all areas. Record details of call point tested | Statutory - Regulatory reform (Fire Safety) Order 2005 Check fire alarm panel for faults Fire alarm audibility test conducted by site with a different call point tested each week in rotation. Number each call point for identification. Check that any fire doors on automatic door closures linked to the fire alarm are closing properly. Check that any doors on exit routes with electro-magnetic/ electro-mechanical locks release when the alarm is activated.
Fire Drill | IN HOUSE | SIX MONTHLY To cover all shift patterns | Statutory - Regulatory reform (Fire Safety) Order 2005 Record details of drill, evacuation time and any problems.
Fire Extinguishers | OUTSIDE CONTRACTOR IN HOUSE | ANNUALLY WEEKLY | Statutory - Regulatory reform (Fire Safety) Order 2005 Weekly in house checks that extinguishers are in place, available for use, undamaged and unobstructed.
Fire Exit Routes | IN HOUSE | WEEKLY MONTHLY | Statutory - Regulatory reform (Fire Safety) Order 2005 Check for any obstructions on escape routes (internally and externally) Doors: check self closing devices, and that push bars/ other emergency fastening devices are operational Check all doors fitted with electromagnetic locks on escape routes are releasing when fire alarm activates.

## Slide 5
AREA | BY WHOM | Period of inspection/ Review | Comments
First Aid Equipment | IN HOUSE | MONTHLY | Health and Safety (first aid) regulations 1981 Regular check to ensure contents are complete and none are outside of expiry date
Fuel Oil Storage | OUTSIDE CONTRACTOR | ANNUALLY | Control of Pollution (Oil Storage) regs 2011 Maintenance check on all oil pipe work
Gas Appliances Boilers, Ovens Etc | OUTSIDE CONTRACTOR | ANNUALLY | Statutory - Gas Safety (Installations and Use) Regs 1998 Gas safety inspection and certificate Annual servicing for efficient operation
Gas Cylinders | IN HOUSE | ANNUALLY | Inspect for damage Regulators should be sent away for testing minimum every 5 years by a specialist contractor
Lifting Lifts And Hoists | OUTSIDE CONTRACTOR | 6 MONTHLY for all lifts, hoists and associated accessories used to lift people and all lifting accessories | Statutory - Lift Operations and Lifting Equipment Regs 1998 (LOLER) Thorough examination maintenance and inspection All lifting accessories (slings, hooks, shackles, ropes etc.) safety eyes and bolts should also be subject to 6 monthly inspections by a competent person
 |  | 12 MONTHLY for all other lifting equipment | 
Lightning Conductors | OUTSIDE CONTRACTOR | ANNUALLY | Lightning conductor to be inspected annually (11 months is actually the recommended frequency – which means over a 12 years the conductor is tested every month allowing for seasonal changes in soil resistivity.) Testing to be carried out to BS 62305:206 comprises : Continuity tests, earth resistance tests, visual check of conductors, bonds and joints and a cert of compliance
Local Exhaust Ventilation Dust Extraction Etc | OUTSIDE CONTRACTOR | EVERY 14 MONTHS | Statutory Control of Substances Hazardous to Health 2002 (COSHH) Verify that extraction is working correctly

## Slide 6
AREA | BY WHOM | Period of inspection/ Review | Comments
Pressure Vessels Compressors, Calorifiers And Air Receivers Etc | Outside Contractor e.g. an insurance company engineer | Periodic inspection and examination determined by a competent person | Statutory - The Pressure Systems Safety Regulations 2000 Written scheme of examination required Pressure vessels associated with a pressurised hot / cold water system should have safety valves tested as part of annual boiler service.
Air Conditioning maintenance and leak checking requirements | OUTSIDE CONTRACTOR | SIX MONTHLY for some units But check with manufacturer for more details | With Covid, check on fresh air flow, and regular cleaning. Some system may only recirculate air and may need to be turned off. Check HSE site. https://www.hse.gov.uk/coronavirus/equipment-and-machinery/air-conditioning-and-ventilation/index.hthttps://www.hse.gov.uk/coronavirus/equipment-and-machinery/air-conditioning-and-ventilation/index.htm
WATER SYSTEM TESTING | IN HOUSE | WEEKLY MONTHLY ANNUALLY | Statutory COSHH , L8 (Control of legionella bacteria in water systems ACOP) Identify and flush seldom used outlets / showers Check water temperature of first and last taps on a circulating system. Cold water taps below 20oC. Hot water taps 50o C. Where thermostatic mixing valves are fitted the temperature should be measured at the valve supply point with a contact thermometer Dismantle, clean/disinfect and descale showerheads and hoses.
Work At Height Ladder Checks Mobile Scaffolding Safety Eyes, Bolts Etc | IN HOUSE IN HOUSE Outside Contractor | SIX MONTHLY SIX MONTHLY ANNUALLY | Complete ladder checklist Towers should only be erected / inspected by trained and competent people. It must be inspected: after assembly in any position; after any event liable to have affected its stability; and at intervals not exceeding seven days. Annual inspection and test to ensure its in safe working order BS 7883 requires that all safety anchor devices are removable for periodic inspection. If the eyebolts installed are intended for rope access use, they will require testing every 6 months. If the eyebolt system is for Fall Arrest, then they should be tested annually (12 months).

## Slide 7
Monitoring of DSE – both at home and at work
eyesight testing and office set up
Monitoring of stress – risk assessment
Mental health
Monitoring of home working
Hearing assessments
Occupational health in general – return of health surveillance
A Few Other Things to Consider……..

## Slide 8
Is your Health & Safety Policy up to date?
Is your Covid 19 risk assessment up to date?
Do your risk assessments take into account the requirements of the Covid 19 risk assessment?
Does your PPE assessment cover Covid 19 requirements?
Is your signage up to date?
Are your racking checks up to date?
And There’s More……..

## Slide 9
For example:
Induction Training
COSHH Training
Manual Handling Training
Correct Wearing of Face Masks
Working at Height Training
Confined Space Working Training
And so on…….
And Then There’s Training……..

## Slide 10
We hope you found this interesting
Thank you for listening
Any questions?